## IP Addresses
Gateway | 192.168.1.1
Subnet | 255.255.255.0
Room | Station | Device | IP Address | Username | Password | TCP/IP Ports
| St1-3 TCs | R1MX1 | 172.16.90.100 |  |  | 502
|  | R1MX2 | 172.16.90.101 |  |  | 921
|  | R1MX3 | 172.16.90.102 |  |  | 922
|  | R1MX4 | 172.16.90.103 |  |  | 923
|  | R1MX5 | 172.16.90.104 |  |  | 924
1 | 1 | APLUS | 172.16.90.105 |  |  | 925
1 | 2 | APLUS | 172.16.90.106 |  |  | 34316
1 | 3 | APLUS | 172.16.90.107
1 | 4 | APLUS | 172.16.90.108
1 | 5 | APLUS | 172.16.90.109
1 | 6 | APLUS | 172.16.90.110
1 | 7 | APLUS | 172.16.90.111
1 | 8 | APLUS | 172.16.90.112
1 |  | Wago | 172.16.90.113 | admin | wago
|  | MX2-1 | 172.16.90.114
|  | MX2-2 | 172.16.90.115
|  | MX2-3 | 172.16.90.116
|  | MX2-4 | 172.16.90.117
|  | MX2-5 | 172.16.90.118
2 | 1 | APLUS | 172.16.90.119
2 | 2 | APLUS | 172.16.90.120
2 | 3 | APLUS | 172.16.90.121
2 | 4 | APLUS | 172.16.90.122
2 | 5 | APLUS | 172.16.90.123
2 | 6 | APLUS | 172.16.90.124
2 | 7 | APLUS | 172.16.90.125
2 | 8 | APLUS | 172.16.90.126
2 |  | Wago | 172.16.90.127 | admin | wago
3 |  | MX3-1 | 172.16.90.128
3 |  | MX3-2 | 172.16.90.129
3 |  | MX3-3 | 172.16.90.130
3 |  | MX3-4 | 172.16.90.131
3 |  | MX3-5 | 172.16.90.132
3 | 1 | APLUS | 172.16.90.133
3 | 2 | APLUS | 172.16.90.134
3 | 3 | APLUS | 172.16.90.135
3 | 4 | APLUS | 172.16.90.136
3 | 5 | APLUS | 172.16.90.137
3 | 6 | APLUS | 172.16.90.138
3 | 7 | APLUS | 172.16.90.139
3 | 8 | APLUS | 172.16.90.140
3 |  | Wago | 172.16.90.141 | admin | wago
4 |  | MX4-1 | 172.16.90.142
4 |  | MX4-2 | 172.16.90.143
4 |  | MX4-3 | 172.16.90.144
4 |  | MX4-4 | 172.16.90.145
4 |  | MX4-5 | 172.16.90.146
4 | 1 | APLUS | 172.16.90.147
4 | 2 | APLUS | 172.16.90.148
4 | 3 | APLUS | 172.16.90.149
4 | 4 | APLUS | 172.16.90.150
4 | 5 | APLUS | 172.16.90.151
4 | 6 | APLUS | 172.16.90.152
4 | 7 | APLUS | 172.16.90.153
4 | 8 | APLUS | 172.16.90.154
4 |  | Wago | 172.16.90.155 | admin | wago

## Wago Setup
| Wago 750-881 |  | PLC - ETHERNET Programmable Fieldbus Controller
Module Number | Module |  | Description | Command Name | Location | Data Type | Values | Output Variable | Location | Data Type | Output Variable | Location | Data Type
1 | 750-430 |  | Input Module, Digital, 8 CH
|  | CH1 | E-Stop Input Reading
|  | CH2 | Door Input
|  | CH3 | Chamber Control Over Temperature Switch
CH4
CH5
CH6
CH7
CH8
2 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
|  | CH8 | Room Interface Box (OK Button)
3 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
|  | CH8 | Room Interface Box (E-Stop Button)
4 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
|  | CH8 | Heat Enable (Chamber Control)
5 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
|  | CH8 | Fan Enable (Chamber Control)
6 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
CH8
7 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
|  | CH8 | Pump Down (Chamber Control)
8 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
CH8
9 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 60Hz Power Relay/Contactor | Yes
|  | CH2 | 50Hz Power Relay/Contactor | Yes
|  | CH3 | 120V Power Relay/Contactor | Yes
|  | CH4 | 240V Power Relay/Contactor | Yes
|  | CH5 | Ground Power Relay/Contactor | Yes
|  | CH6 | Ground Neutral Power Relay/Contactor | Yes
|  | CH7 | Ground Leakage | Yes
CH8
10 | 750-602 |  | 24VDC Power Supply
11 | 750-530 |  | Output Module, Digital, 8 CH
|  |  | Door Enable | Rm1OpenerCmd | %IW353 | WORD | 0,1
|  | CH1 | 24VDC Freezer Relay | Rm1St1Dr1Cmd | %IW304 | WORD |  | Rm1St1Dr1 | %QX8.0 | BOOL | Rm1St1Dr1Stat | %QW302 | Word
|  | CH2 | 24VDC Cabinet Relay | Rm1St1Dr2Cmd | %IW312 | WORD
|  | CH3 | 24VDC Drawer Relay | Rm1St1Dr3Cmd | %IW320 | WORD
|  | CH4 | 24VDC Freezer Relay | Rm1St2Dr1Cmd | %IW305 | WORD |  | Rm1St2Dr1 | %QX8.3 | BOOL | Rm1St2Dr1Stat | %QW305 | Word
|  | CH5 | 24VDC Cabinet Relay | Rm1St2Dr2Cmd | %IW313 | WORD
|  | CH6 | 24VDC Drawer Relay | Rm1St2Dr3Cmd | %IW321 | WORD
|  | CH7 | 24VDC Freezer Relay | Rm1St3Dr1Cmd | %IW306 | WORD |  | Rm1St3Dr1 | %QX8.6 | BOOL | Rm1St3Dr1Stat | %QW308 | Word
|  | CH8 | 24VDC Cabinet Relay | Rm1St3Dr2Cmd | %IW314 | WORD
12 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 24VDC Drawer Relay | Rm1St3Dr3Cmd | %IW322 | WORD
|  | CH2 | 24VDC Freezer Relay | Rm1St4Dr1Cmd | %IW307 | WORD |  | Rm1St4Dr1 | %QX8.9 | BOOL | Rm1St4Dr1Stat | %QW311 | Word
|  | CH3 | 24VDC Cabinet Relay | Rm1St4Dr2Cmd | %IW315 | WORD
|  | CH4 | 24VDC Drawer Relay | Rm1St4Dr3Cmd | %IW323 | WORD
|  | CH5 | 24VDC Freezer Relay | Rm1St5Dr1Cmd | %IW308 | WORD |  | Rm1St5Dr1 | %QX8.12 | BOOL | Rm1St5Dr1Stat | %QW314 | Word
|  | CH6 | 24VDC Cabinet Relay | Rm1St5Dr2Cmd | %IW316 | WORD
|  | CH7 | 24VDC Drawer Relay | Rm1St5Dr3Cmd | %IW324 | WORD
|  | CH8 | 24VDC Freezer Relay | Rm1St6Dr1Cmd | %IW309 | WORD |  | Rm1St6Dr1 | %QX8.15 | BOOL | Rm1St6Dr1Stat | %QW317 | Word
13 | 750-530 |  | Output Module, Digital, 8 CH
|  | CH1 | 24VDC Cabinet Relay | Rm1St6Dr2Cmd | %IW317 | WORD
|  | CH2 | 24VDC Drawer Relay | Rm1St6Dr3Cmd | %IW325 | WORD
|  | CH3 | 24VDC Freezer Relay | Rm1St7Dr1Cmd | %IW310 | WORD |  | Rm1St7Dr1 | %QX9.2 | BOOL | Rm1St7Dr1Stat | %QW320 | Word
|  | CH4 | 24VDC Cabinet Relay | Rm1St7Dr2Cmd | %IW318 | WORD
|  | CH5 | 24VDC Drawer Relay | Rm1St7Dr3Cmd | %IW326 | WORD
|  | CH6 | 24VDC Freezer Relay | Rm1St8Dr1Cmd | %IW311 | WORD |  | Rm1St8Dr1 | %QX9.5 | BOOL | Rm1St8Dr1Stat | %QW323 | Word
|  | CH7 | 24VDC Cabinet Relay | Rm1St8Dr2Cmd | %IW319 | WORD
|  | CH8 | 24VDC Drawer Relay | Rm1St8Dr3Cmd | %IW327 | WORD
14 | 750-602 |  | 24VDC Power Supply
15 | 750-453 |  | 4-Channel Analog Input Module 0/4-20 mA
|  | CH1 | 0-20mA Voltage Stall 1 (Low Range) | fwS1Volt1
|  | CH2 | 0-20mA Current Stall 1 (High Range) | fwS1Volt2
|  | CH3 | 0-20mA Voltage Stall 2 (Low Range) | fwS2Volt1
|  | CH4 | 0-20mA Current Stall 2 (High Range) | fwS2Volt2
16 | 750-453 |  | 4-Channel Analog Input Module 0/4-20 mA
|  | CH1 | 0-20mA Voltage Stall 3 (Low Range) | fwS3Volt1
|  | CH2 | 0-20mA Current Stall 3 (High Range) | fwS3Volt2
|  | CH3 | 0-20mA Voltage Stall 4 (Low Range) | fwS4Volt1
|  | CH4 | 0-20mA Current Stall 4 (High Range) | fwS4Volt2
17 | 750-453 |  | 4-Channel Analog Input Module 0/4-20 mA
|  | CH1 | 0-20mA Voltage Stall 5 (Low Range) | fwS5Volt1
|  | CH2 | 0-20mA Current Stall 5 (High Range) | fwS5Volt2
|  | CH3 | 0-20mA Voltage Stall 6 (Low Range) | fwS6Volt1
|  | CH4 | 0-20mA Current Stall 6 (High Range) | fwS6Volt2
18 | 750-453 |  | 4-Channel Analog Input Module 0/4-20 mA
|  | CH1 | 0-20mA Voltage Stall 7 (Low Range) | fwS7Volt1
|  | CH2 | 0-20mA Current Stall 7 (High Range) | fwS7Volt2
|  | CH3 | 0-20mA Voltage Stall 8 (Low Range) | fwS8Volt1
|  | CH4 | 0-20mA Current Stall 8 (High Range) | fwS8Volt2
19 | 750-453 |  | 4-Channel Analog Input Module 0/4-20 mA
|  | CH1 | 0-20mA Rotronic Temperature
|  | CH2 | 0-20mA Rotronic Humidity
CH3
CH4
20 | 750-553 |  | 4-Channel Analog Output Module 0/4-20 mA
|  | CH1 | Chamber Control (TBAHA)
|  | CH2 | Chamber Control (Steam Supply Valve)
|  | CH3 | Chamber Control (Sensible Upper Coil)
|  | CH4 | Chamber Control (Latent Coil)
21 | 750-469 |  | 2-channel analog input; Thermocouple K;
|  | CH1 | Chamber Control (Supply Temperature)
|  | CH2 | Chamber Control (Sensible Coil Face Temperature)
22 | 750-469 |  | 2-channel analog input; Thermocouple K;
|  | CH1 | Chamber Control (Latent Coil Face Temp)
CH2
23 | 750-612 |  | Supply Module 0-230V AC/DC (120V Internal Bus Supply)
24 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 1
|  | CH2 | Decrease (Motor Variac) - Stall 1
25 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 2
|  | CH2 | Decrease (Motor Variac) - Stall 2
26 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 3
|  | CH2 | Decrease (Motor Variac) - Stall 3
27 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 4
|  | CH2 | Decrease (Motor Variac) - Stall 4
28 | 750-612 |  | Supply Module 0-230V AC/DC
| 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 5
|  | CH2 | Decrease (Motor Variac) - Stall 5
29 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 6
|  | CH2 | Decrease (Motor Variac) - Stall 6
30 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 7
|  | CH2 | Decrease (Motor Variac) - Stall 7
31 | 750-509 |  | 2-Channel Digital Output Module 230 VAC/DC, with Solid State Relay 0.3 A
|  | CH1 | Increase (Motor Variac) - Stall 8
|  | CH2 | Decrease (Motor Variac) - Stall 8
32 | 750-600 |  | End Module

## Wago Price
Manufacturer | P/N | Qty | Price | Total | Ebay Price | Total Ebay | AirHydro Power | 750-430 | 750-453 | 750-469 | 750-509 | 750-530 | 750-553 | 750-600 | 750-602 | 750-612
Wago | 750-881 | 1 | 910.33 | 910.33 | 375 | 375 |  |  | 750-453 | 750-469 | 750-509 | 750-530 |  |  | 750-602 | 750-612
Wago | 750-430 | 1 | 124.16 | 124.16 | 43 | 43 |  |  | 750-453 |  | 750-509 | 750-530
Wago | 750-453 | 5 | 468.25 | 2341.25 | 168 | 840 |  |  | 750-453 |  | 750-509 | 750-530
Wago | 750-469/0000-0002 | 2 | 560.81 | 1121.62 | 357.53 | 715.06 |  |  | 750-453 |  | 750-509 | 750-530
Wago | 750-509 | 8 | 170.73 | 1365.84 | 63.5 | 508 |  |  |  |  | 750-509 | 750-530
Wago | 750-530 | 11 | 139.76 | 1537.36 | 67 | 737 |  |  |  |  | 750-509 | 750-530
Wago | 750-553 | 1 | 505.96 | 505.96 | 298.3 | 298.3 |  |  |  |  | 750-509 | 750-530
Wago | 750-600 | 1 | 34.27 | 34.27 | 11 | 11 | [5 empty] | 750-530
Wago | 750-602 | 2 | 47.01 | 94.02 | 20 | 40 | [5 empty] | 750-530
Wago | 750-612 | 2 | 46.58 | 93.16 | 15 | 30 | [5 empty] | 750-530
|  |  |  | 8127.97 |  | 3597.36 | 5204.17

## Wago Modbus Variables
Input Variables | [6 empty] | Output Variables | [5 empty] | Physical Input Variables |  |  |  |  | Physical Output Variables (Add 200hex to Modbus Address)
Variable Name | Modbus Location | Data Type | Add 200 Hex | Set Value | Working |  | Variable Name | Modbus Location | Add 200 Hex | Data Type | Read/Write | COM Status | Variable Name | Modbus Location | Data Type | Read/Write | COM Status | Variable Name | Modbus Location | Add 200 Hex | Data Type | Read/Write | COM Status
fwS1Volt1 | %IW0 | Word | [10 empty] | fbEstop | %IX24.0 | BOOL |  | Maybe | twHeatCtrl | %QW0 | 512 | Word
fwS1Volt2 | %IW1 | Word | [10 empty] | fbDoors | %IX24.1 | BOOL |  | Maybe | twSteamCtrl | %QW1 | 513 | Word
fwS2Volt1 | %IW2 | Word | [10 empty] | fbSafety | %IX24.2 | BOOL |  | Maybe | twCoolCtrl | %QW2 | 514 | Word
fwS2Volt2 | %IW3 | Word | [15 empty] | twDehumCtrl | %QW3 | 515 | Word
fwS3Volt1 | %IW4 | Word
fwS3Volt2 | %IW5 | Word | [15 empty] | tbSt1Pwr60 | %QX4.0 | 516 | BOOL | Output Word 4
fwS4Volt1 | %IW6 | Word | [15 empty] | tbSt1Pwr50 | %QX4.1 | 516.1 | BOOL
fwS4Volt2 | %IW7 | Word | [15 empty] | tbSt1Pwr120 | %QX4.2 | 516.2 | BOOL
fwS5Volt1 | %IW8 | Word | [15 empty] | tbSt1Pwr240 | %QX4.3 | 516.3 | BOOL
fwS5Volt2 | %IW9 | Word | [15 empty] | tbSt1GndLine | %QX4.4 | 516.4 | BOOL
fwS6Volt1 | %IW10 | Word | [15 empty] | tbSt1GndNeu | %QX4.5 | 516.5 | BOOL
fwS6Volt2 | %IW11 | Word | [15 empty] | tbSt1GndLeak | %QX4.6 | 516.6 | BOOL
fwS7Volt1 | %IW12 | Word | [15 empty] | tbRmOk | %QX4.7 | 516.7 | BOOL
fwS7Volt2 | %IW13 | Word | [15 empty] | tbSt1Pwr60 | %QX4.8 | 516.8 | BOOL
fwS8Volt1 | %IW14 | Word | [15 empty] | tbSt1Pwr50 | %QX4.9 | 516.9 | BOOL
fwS8Volt2 | %IW15 | Word | [15 empty] | tbSt1Pwr120 | %QX4.10 | 516.1 | BOOL
fwRoomHum | %IW16 | Word |  |  | Yes | [12 empty] | tbSt1Pwr240 | %QX4.11 | 516.11 | BOOL
fwRoomTemp | %IW17 | Word |  |  | Yes | [12 empty] | tbSt1GndLine | %QX4.12 | 516.12 | BOOL
fwAISpare1 | %IW18 | Word | [15 empty] | tbSt1GndNeu | %QX4.13 | 516.13 | BOOL
fwAISpare2 | %IW19 | Word | [15 empty] | tbSt1GndLeak | %QX4.14 | 516.14 | BOOL
fwSuppTemp | %IW20 | INT |  |  | Yes | [12 empty] | tbFault | %QX4.15 | 516.15 | BOOL
fwCoolTemp | %IW21 | INT |  |  | Yes | [12 empty] | tbSt1Pwr60 | %QX5.0 | 517 | BOOL | Output Word 5
fwDehumTemp | %IW22 | INT |  |  | Yes | [12 empty] | tbSt1Pwr50 | %QX5.1 | 517.1 | BOOL
fwUnused | %IW23 | INT |  |  | This is the Glycol. Not Used | [12 empty] | tbSt1Pwr120 | %QX5.2 | 517.2 | BOOL
[18 empty] | tbSt1Pwr240 | %QX5.3 | 517.3 | BOOL
gwVoltRate1 | %IW256 | Word |  |  | Yes | [12 empty] | tbSt1GndLine | %QX5.4 | 517.4 | BOOL
gwVoltRate2 | %IW257 | Word |  |  | Yes | [12 empty] | tbSt1GndNeu | %QX5.5 | 517.5 | BOOL
gwVoltRate3 | %IW258 | Word |  |  | Yes | [12 empty] | tbSt1GndLeak | %QX5.6 | 517.6 | BOOL
gwVoltRate4 | %IW259 | Word |  |  | Yes | [12 empty] | tbRmHeat | %QX5.7 | 517.7 | BOOL
gwVoltRate5 | %IW260 | Word |  |  | Yes | [12 empty] | tbSt1Pwr60 | %QX5.8 | 517.8 | BOOL
gwVoltRate6 | %IW261 | Word |  |  | Yes | [12 empty] | tbSt1Pwr50 | %QX5.9 | 517.9 | BOOL
gwVoltRate7 | %IW262 | Word |  |  | Yes | [12 empty] | tbSt1Pwr120 | %QX5.10 | 517.1 | BOOL
gwVoltRate8 | %IW263 | Word |  |  | Yes | [12 empty] | tbSt1Pwr240 | %QX5.11 | 517.11 | BOOL
gwVoltWindow1 | %IW264 | Word |  |  | Yes | [12 empty] | tbSt1GndLine | %QX5.12 | 517.12 | BOOL
gwVoltWindow2 | %IW265 | Word |  |  | Yes | [12 empty] | tbSt1GndNeu | %QX5.13 | 517.13 | BOOL
gwVoltWindow3 | %IW266 | Word |  |  | Yes | [12 empty] | tbSt1GndLeak | %QX5.14 | 517.14 | BOOL
gwVoltWindow4 | %IW267 | Word |  |  | Yes | [12 empty] | tbRmBlower | %QX5.15 | 517.15 | BOOL
gwVoltWindow5 | %IW264 | Word |  |  | Yes | [12 empty] | tbSt1Pwr60 | %QX6.0 | 518 | BOOL | Output Word 6
gwVoltWindow6 | %IW265 | Word |  |  | Yes | [12 empty] | tbSt1Pwr50 | %QX6.1 | 518.1 | BOOL
gwVoltWindow7 | %IW266 | Word |  |  | Yes | [12 empty] | tbSt1Pwr120 | %QX6.2 | 518.2 | BOOL
gwVoltWindow8 | %IW267 | Word |  |  | Yes | [12 empty] | tbSt1Pwr240 | %QX6.3 | 518.3 | BOOL
fwVoltSet1 | %IW272 | Word |  |  | Yes |  | twVoltMon1 | %QW272 | 784 | Word |  | Yes | [5 empty] | tbSt1GndLine | %QX6.4 | 518.4 | BOOL
fwVoltSet2 | %IW273 | Word |  |  | Yes |  | twVoltMon2 | %QW273 | 785 | Word |  | Yes | [5 empty] | tbSt1GndNeu | %QX6.5 | 518.5 | BOOL
fwVoltSet3 | %IW274 | Word |  |  | Yes |  | twVoltMon3 | %QW274 | 786 | Word |  | Yes | [5 empty] | tbSt1GndLeak | %QX6.6 | 518.6 | BOOL
fwVoltSet4 | %IW275 | Word |  |  | Yes |  | twVoltMon4 | %QW275 | 787 | Word |  | Yes | [5 empty] | tbSpareOut1 | %QX6.7 | 518.7 | BOOL
fwVoltSet5 | %IW276 | Word |  |  | Yes |  | twVoltMon5 | %QW276 | 788 | Word |  | Yes | [5 empty] | tbSt1Pwr60 | %QX6.8 | 518.8 | BOOL
fwVoltSet6 | %IW277 | Word |  |  | Yes |  | twVoltMon6 | %QW277 | 789 | Word |  | Yes | [5 empty] | tbSt1Pwr50 | %QX6.9 | 518.9 | BOOL
fwVoltSet7 | %IW278 | Word |  |  | Yes |  | twVoltMon7 | %QW278 | 790 | Word |  | Yes | [5 empty] | tbSt1Pwr120 | %QX6.10 | 518.1 | BOOL
fwVoltSet8 | %IW279 | Word |  |  | Yes |  | twVoltMon8 | %QW279 | 791 | Word |  | Yes | [5 empty] | tbSt1Pwr240 | %QX6.11 | 518.11 | BOOL
fwVoltRng1 | %IW280 | Word |  |  | Yes |  | twVoltStat1 | %QW280 | 792 | Word |  | Yes | [5 empty] | tbSt1GndLine | %QX6.12 | 518.12 | BOOL
fwVoltRng2 | %IW281 | Word |  |  | Yes |  | twVoltStat2 | %QW281 | 793 | Word |  | Yes | [5 empty] | tbSt1GndNeu | %QX6.13 | 518.13 | BOOL
fwVoltRng3 | %IW282 | Word |  |  | Yes |  | twVoltStat3 | %QW282 | 794 | Word |  | Yes | [5 empty] | tbSt1GndLeak | %QX6.14 | 518.14 | BOOL
fwVoltRng4 | %IW283 | Word |  |  | Yes |  | twVoltStat4 | %QW283 | 795 | Word |  | Yes | [5 empty] | tbRmPumpRun | %QX6.15 | 518.15 | BOOL
fwVoltRng5 | %IW284 | Word |  |  | Yes |  | twVoltStat5 | %QW284 | 796 | Word |  | Yes | [5 empty] | tbSt1Pwr60 | %QX7.0 | 519 | BOOL | Output Word 7
fwVoltRng6 | %IW285 | Word |  |  | Yes |  | twVoltStat6 | %QW285 | 797 | Word |  | Yes | [5 empty] | tbSt1Pwr50 | %QX7.1 | 519.1 | BOOL
fwVoltRng7 | %IW286 | Word |  |  | Yes |  | twVoltStat7 | %QW286 | 798 | Word |  | Yes | [5 empty] | tbSt1Pwr120 | %QX7.2 | 519.2 | BOOL
fwVoltRng8 | %IW287 | Word |  |  | Yes |  | twVoltStat8 | %QW287 | 799 | Word |  | Yes | [5 empty] | tbSt1Pwr240 | %QX7.3 | 519.3 | BOOL
fwVoltPol1 | %IW296 | Word |  |  | Yes |  |  |  | 808 | Word | [7 empty] | tbSt1GndLine | %QX7.4 | 519.4 | BOOL
fwVoltPol2 | %IW297 | Word |  |  | Yes |  |  |  | 809 | Word | [7 empty] | tbSt1GndNeu | %QX7.5 | 519.5 | BOOL
fwVoltPol3 | %IW298 | Word |  |  | Yes |  |  |  | 810 | Word | [7 empty] | tbSt1GndLeak | %QX7.6 | 519.6 | BOOL
fwVoltPol4 | %IW299 | Word |  |  | Yes |  |  |  | 811 | Word | [7 empty] | tbSpareOut2 | %QX7.7 | 519.7 | BOOL
fwVoltPol5 | %IW300 | Word |  |  | Yes |  |  |  | 812 | Word | [7 empty] | tbSt1Pwr60 | %QX7.8 | 519.8 | BOOL
fwVoltPol6 | %IW301 | Word |  |  | Yes |  |  |  | 813 | Word | [7 empty] | tbSt1Pwr50 | %QX7.9 | 519.9 | BOOL
fwVoltPol7 | %IW302 | Word |  |  | Yes |  |  | %QW302 | 814 | Word | [7 empty] | tbSt1Pwr120 | %QX7.10 | 519.1 | BOOL
fwVoltPol8 | %IW303 | Word |  |  | Yes |  |  | %QW303 | 815 | Word | [7 empty] | tbSt1Pwr240 | %QX7.11 | 519.1 | BOOL
Rm1St1Dr1Cmd | %IW304 | Word |  |  | Yes | Rm1St1Dr1Stat | Rm1St1Dr1Stat | %QW304 | 816 | Word | [7 empty] | tbSt1GndLine | %QX7.12 | 519.12 | BOOL
Rm1St2Dr1Cmd | %IW305 | Word |  |  | Yes | Rm1St2Dr1Stat | Rm1St1Dr2Stat | %QW305 | 817 | Word | [7 empty] | tbSt1GndNeu | %QX7.13 | 519.13 | BOOL
Rm1St3Dr1Cmd | %IW306 | Word |  |  | Yes | Rm1St3Dr1Stat | Rm1St1Dr3Stat | %QW306 | 818 | Word | [7 empty] | tbSt1GndLeak | %QX7.14 | 519.14 | BOOL
Rm1St4Dr1Cmd | %IW307 | Word |  |  | Yes | Rm1St4Dr1Stat | Rm1St2Dr1Stat | %QW307 | 819 | Word | [7 empty] | tbSpareOut3 | %QX7.15 | 519.15 | BOOL
Rm1St5Dr1Cmd | %IW308 | Word |  |  | Yes | Rm1St5Dr1Stat | Rm1St2Dr2Stat | %QW308 | 820 | Word | [7 empty] | Rm1St1Dr1 | %QX8.0 | 520 | BOOL | Output Word 8
Rm1St6Dr1Cmd | %IW309 | Word |  |  | Yes | Rm1St6Dr1Stat | Rm1St2Dr3Stat | %QW309 | 821 | Word | [7 empty] | Rm1St1Dr2 | %QX8.1 | 520.1 | BOOL
Rm1St7Dr1Cmd | %IW310 | Word |  |  | Yes | Rm1St7Dr1Stat | Rm1St3Dr1Stat | %QW310 | 822 | Word | [7 empty] | Rm1St1Dr3 | %QX8.2 | 520.2 | BOOL
Rm1St8Dr1Cmd | %IW311 | Word |  |  | Yes | Rm1St8Dr1Stat | Rm1St3Dr2Stat | %QW311 | 823 | Word | [7 empty] | Rm1St2Dr1 | %QX8.3 | 520.3 | BOOL
Rm1St1Dr2Cmd | %IW312 | Word |  |  | Yes | Rm1St1Dr2Stat | Rm1St3Dr3Stat | %QW312 | 824 | Word | [7 empty] | Rm1St2Dr2 | %QX8.4 | 520.4 | BOOL
Rm1St2Dr2Cmd | %IW313 | Word |  |  | Yes | Rm1St2Dr2Stat | Rm1St4Dr1Stat | %QW313 | 825 | Word | [7 empty] | Rm1St2Dr3 | %QX8.5 | 520.5 | BOOL
Rm1St3Dr2Cmd | %IW314 | Word |  |  | Yes | Rm1St3Dr2Stat | Rm1St4Dr2Stat | %QW314 | 826 | Word | [7 empty] | Rm1St3Dr1 | %QX8.6 | 520.6 | BOOL
Rm1St4Dr2Cmd | %IW315 | Word |  |  | Yes | Rm1St4Dr2Stat | Rm1St4Dr3Stat | %QW315 | 827 | Word | [7 empty] | Rm1St3Dr2 | %QX8.7 | 520.7 | BOOL
Rm1St5Dr2Cmd | %IW316 | Word |  |  | Yes | Rm1St5Dr2Stat | Rm1St5Dr1Stat | %QW316 | 828 | Word | [7 empty] | Rm1St3Dr3 | %QX8.8 | 520.8 | BOOL
Rm1St6Dr2Cmd | %IW317 | Word |  |  | Yes | Rm1St6DrStat | Rm1St5Dr2Stat | %QW317 | 829 | Word | [7 empty] | Rm1St4Dr1 | %QX8.9 | 520.9 | BOOL
Rm1St7Dr2Cmd | %IW318 | Word |  |  | Yes | Rm1St7Dr2Stat | Rm1St5Dr3Stat | %QW318 | 830 | Word | [7 empty] | Rm1St4Dr2 | %QX8.10 | 520.1 | BOOL
Rm1St8Dr2Cmd | %IW319 | Word |  |  | Yes | Rm1St8Dr2Stat | Rm1St6Dr1Stat | %QW319 | 831 | Word | [7 empty] | Rm1St4Dr3 | %QX8.11 | 520.11 | BOOL
Rm1St1Dr3Cmd | %IW320 | Word |  |  | Yes | Rm1St1Dr3Stat | Rm1St6Dr2Stat | %QW320 | 832 | Word | [7 empty] | Rm1St5Dr1 | %QX8.12 | 520.12 | BOOL
Rm1St2Dr3Cmd | %IW321 | Word |  |  | Yes | Rm1St2Dr3Stat | Rm1St6Dr3Stat | %QW321 | 833 | Word | [7 empty] | Rm1St5Dr2 | %QX8.13 | 520.13 | BOOL
Rm1St3Dr3Cmd | %IW322 | Word |  |  | Yes | Rm1St3Dr3Stat | Rm1St7Dr1Stat | %QW322 | 834 | Word | [7 empty] | Rm1St5Dr3 | %QX8.14 | 520.14 | BOOL
Rm1St4Dr3Cmd | %IW323 | Word |  |  | Yes | Rm1St4Dr3Stat | Rm1St7Dr2Stat | %QW323 | 835 | Word | [7 empty] | Rm1St6Dr1 | %QX8.15 | 520.15 | BOOL
Rm1St5Dr3Cmd | %IW324 | Word |  |  | Yes | Rm1St5Dr3Stat | Rm1St7Dr3Stat | %QW324 | 836 | Word | [7 empty] | Rm1St6Dr2 | %QX9.0 | 521 | BOOL | Output Word 9
Rm1St6Dr3Cmd | %IW325 | Word |  |  | Yes | Rm1St6Dr3Stat | Rm1St8Dr1Stat | %QW325 | 837 | Word | [7 empty] | Rm1St6Dr3 | %QX9.1 | 521.1 | BOOL
Rm1St7Dr3Cmd | %IW326 | Word |  |  | Yes | Rm1St7Dr3Stat | Rm1St8Dr2Stat | %QW326 | 838 | Word | [7 empty] | Rm1St7Dr1 | %QX9.2 | 521.2 | BOOL
Rm1St8Dr3Cmd | %IW327 | Word |  |  | Yes | Rm1St8Dr3Stat | Rm1St8Dr3Stat | %QW327 | 839 | Word | [7 empty] | Rm1St7Dr2 | %QX9.3 | 521.3 | BOOL
fwRmTempSP | %IW328 | Word | 840 |  |  |  | twRoomTemp | %QW328 |  | Word |  | Yes | [5 empty] | Rm1St7Dr3 | %QX9.4 | 521.4 | BOOL
fwRmHumSP | %IW329 | Word | 841 |  |  |  | twRoomHum | %QW329 |  | Word |  | Yes | [5 empty] | Rm1St8Dr1 | %QX9.5 | 521.5 | BOOL
fwCoolTempSP | %IW330 | Word | 842 |  |  |  | twSuppTemp | %QW330 |  | Word |  | Yes | [5 empty] | Rm1St8Dr2 | %QX9.6 | 521.6 | BOOL
fwDehumTempSP | %IW331 | Word | 843 |  |  |  | twCoolTemp | %QW331 |  | Word |  | Yes | [5 empty] | Rm1St8Dr3 | %QX9.7 | 521.7 | BOOL
fwRmRun | %IW332 | Word | 844 |  | Yes |  | twDehumTemp | %QW332 |  | Word |  | Yes | [5 empty] | tbS1VoltInc | %QX9.8 | 521.8 | BOOL
fwRmOk | %IW333 | Word | 845 |  | Yes |  | twGlycolTemp | %QW333 |  | Word |  | Yes | [5 empty] | tbS1VoltDec | %QX9.9 | 521.9 | BOOL
fwTesting | %IW334 | Word | 846 |  | Not Listed in PLC Program |  | twHeatRate | %QW334 |  | Word |  | Yes | [5 empty] | tbS2VoltInc | %QX9.10 | 521.1 | BOOL
fwRmDryP | %IW335 | Word | 847 | 200 | Yes |  | twSteamRate | %QW335 |  | Word |  | Yes | [5 empty] | tbS2VoltDec | %QX9.11 | 521.11 | BOOL
fwRmDryI | %IW336 | Word | 848 | 15000 | Yes |  | twCoolRate | %QW336 |  | Word |  | Yes | [5 empty] | tbS3VoltInc | %QX9.12 | 521.12 | BOOL
fwRmHumP | %IW337 | Word | 849 | 400 | Yes |  | twDehumRate | %QW337 |  | Word |  | Yes | [5 empty] | tbS3VoltDec | %QX9.13 | 521.13 | BOOL
fwRmHumI | %IW338 | Word | 850 | 15000 | Yes |  | twStatus | %QW338 |  | Word |  | Yes | [5 empty] | tbS4VoltInc | %QX9.14 | 521.14 | BOOL
fwRmHeatP | %IW339 | Word | 851 | 1000 | Yes |  | twDoorEna | %QW339 |  | Word |  | Yes | [5 empty] | tbS4VoltDec | %QX9.15 | 521.15 | BOOL
fwRmHeatI | %IW340 | Word | 852 | 2000 | Yes | [12 empty] | tbS5VoltInc | %QX10.0 | 522 | BOOL | Output Word 10
fwCoolTempP | %IW341 | Word | 853 | 500 | Yes | [12 empty] | tbS5VoltDec | %QX10.1 | 522.1 | BOOL
fwCoolTempI | %IW342 | Word | 854 | 6000 | Yes | [12 empty] | tbS6VoltInc | %QX10.2 | 522.2 | BOOL
fwDehumTempP | %IW343 | Word | 855 | 500 | Yes | [12 empty] | tbS6VoltDec | %QX10.3 | 522.3 | BOOL
fwDehumTempI | %IW344 | Word | 856 | 6000 | Yes | [12 empty] | tbS7VoltInc | %QX10.4 | 522.4 | BOOL
fwGndLeak1 | %IW345 | Word | 857 |  | Yes | [12 empty] | tbS7VoltDec | %QX10.5 | 522.5 | BOOL
fwGndLeak2 | %IW346 | Word | 858 |  | Yes | [12 empty] | tbS8VoltInc | %QX10.6 | 522.6 | BOOL
fwGndLeak3 | %IW347 | Word | 859 |  | Yes | [12 empty] | tbS8VoltDec | %QX10.7 | 522.7 | BOOL
fwGndLeak4 | %IW348 | Word | 860 |  | Yes
fwGndLeak5 | %IW349 | Word | 861 |  | Yes
fwGndLeak6 | %IW350 | Word | 862 |  | Yes
fwGndLeak7 | %IW351 | Word | 863 |  | Yes
fwGndLeak8 | %IW352 | Word | 864 |  | Yes
Rm1OpenerCmd | %IW353 | Word | 865 |  | Yes
Note on A44: GE User: multiply standard voltage by 100
Note on A52: GE User: Range 1-4

## Modbus Variables
Inputs | Outputs
Physical IO Modules
0
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
24
Modbus Registers
256
257
258
259
260
261
262
263
264
265
266
267
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
Modbus Output Registers 0x0200 Add
512
513
514
515
516
517
518
519
520
521
522
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
840
841
842
843
844
845
846
847
848
849
850
851